PV System Design

- Load Analysis:

- For Nursing Building

| LOAD | QTY. | POWER (W) | TOTAL POWER (W) | HRS. USED | DAILY CONSUMPTION (WH) |
| --- | --- | --- | --- | --- | --- |
| LIGHT BULB | 22 | 8 | 176 | 8 | 1408 |
| FLOURESCENT TUBE | 92 | 20 | 1840 | 8 | 14720 |
| CEILING FAN | 10 | 80 | 800 | 8 | 6400 |
| PC | 8 | 100 | 800 | 5 | 4000 |
| PRINTER | 3 | 12 | 36 | 2 | 72 |
| WATER DISPENSER | 2 | 300 | 600 | 8 | 4800 |
| TV | 2 | 120 | 240 | 3 | 720 |
| REF | 1 | 77 | 77 | 24 | 1848 |
| COFFE MAKER | 1 | 750 | 750 | 0.167 | 125.25 |
| SPEAKER | 1 | 650 | 650 | 6 | 3900 |
| ELECTRIC BED | 1 | 100 | 100 | 4 | 400 |
| CCTV | 2 | 6 | 12 | 24 | 288 |
| ELECTRIC STOVE | 1 | 1200 | 1200 | 0.5 | 600 |
| PRINTER WF-C878R | 1 | 40 | 40 | 3 | 120 |
| Inverter Floor Mounted Aircon | 3 | 3600 | 10800 | 4 | 43200 |
| AIRCON (WINDOW TYPE) | 6 | 850 | 5100 | 4 | 20400 |
| AIRCON (SPLIT TYPE) | 1 | 1500 | 1500 | 4 | 6000 |
| EMERGENCY LIGHT | 1 | 3 | 3 | 24 | 72 |
| TOTAL | - | - | 24721 | - | 109,073.25 |

| LOAD | QTY. | POWER (W) | TOTAL POWER (W) | HRS. USED | DAILY CONSUMPTION (WH) |
| --- | --- | --- | --- | --- | --- |
| LIGHT BULB | 85 | 8 | 680 | 8 | 5440 |
| ELECTRIC FAN (1) | 1 | 300 | 300 | 8 | 2400 |
| ELECTRIC FAN (2) | 9 | 70 | 630 | 8 | 5040 |
| WATER DISPENSER | 2 | 300 | 600 | 11 | 6600 |
| TV | 1 | 120 | 120 | 3 | 360 |
| CCTV | 2 | 6 | 12 | 24 | 288 |
| TELEPHONE | 1 | 3 | 3 | 1 | 3 |
| PC | 14 | 100 | 1400 | 6 | 8400 |
| PRINTER (1) | 3 | 12 | 36 | 3 | 108 |
| PRINTER (2) | 1 | 170 | 170 | 3 | 510 |
| EMERGENCY LIGHT | 1 | 3 | 3 | 24 | 72 |
| EVAPORATIVE AIR COOLER | 1 | 150 | 150 | 7 | 1050 |
| AIRCON (WINDOW TYPE) | 10 | 850 | 8500 | 4 | 34000 |
| AIRCON (SPLIT TYPE) | 1 | 1500 | 1500 | 4 | 6000 |
| LAPTOP | 2 | 50 | 100 | 5 | 500 |
| PROJECTOR | 1 | 200 | 200 | 4 | 800 |
| ELECTRIC STOVE | 1 | 1200 | 1200 | 0.5 | 600 |
| TOTAL | - | - | 15604 | - | 72,171 |

- For Usso Building

| LOAD | QTY. | POWER (W) | TOTAL POWER (W) | HRS. USED | DAILY CONSUMPTION (WH) |
| --- | --- | --- | --- | --- | --- |
| AIRCON | 3 | 2400 | 7200 | 4 | 28800 |
| REF | 1 | 130 | 130 | 24 | 3120 |
| PC | 8 | 100 | 800 | 6 | 4800 |
| LAPTOP | 6 | 50 | 300 | 4 | 1200 |
| STAND FAN | 5 | 70 | 350 | 10 | 3500 |
| INDUSTRIAL FAN | 2 | 350 | 700 | 10 | 7000 |
| LIGHT BULB | 37 | 8 | 296 | 8 | 2368 |
| FLOURESCENT TUBE | 4 | 20 | 80 | 8 | 640 |
| PRINTER | 9 | 12 | 108 | 3 | 324 |
| TOLAGO CEILING LIGHT | 1 | 46 | 46 | 5 | 230 |
| TELEPHONE | 3 | 3 | 9 | 1 | 9 |
| WATER DISPENSER | 2 | 300 | 600 | 11 | 6600 |
| EMERGENCY LIGHTS | 5 | 3 | 15 | 24 | 360 |
| CCTV (HIK VISION) | 1 | 6 | 6 | 24 | 144 |
| COFFE MAKER | 1 | 550 | 550 | 0.167 | 91.85 |
| BREAD TOASTER | 1 | 1500 | 1500 | 0.05 | 75 |
| TV | 1 | 120 | 120 | 7 | 840 |
| AIR PURIFIER | 2 | 40 | 80 | 6 | 480 |
| TOTAL | - | - | 12890 | - | 60,581.85 |

- For Vpsas Building

Total Daily Consumption = 241,826.1 W-H

- Sizing Of PV Panels:

PV Power =Total Daily ConsumptionSun Peak Hours x 1.3

PV Power = 241,826.1 WH4HOURS x 1.3 = 78593.4825W

No. of panels = PV PowerRating of PV

No. of panels = 78593.4825W600W ≈ 131 pcs

- Use 131 pcs-600 Watts JA Solar Monocrystalline Solar Panels

Total Minimum Plot Size: 26mx21m (546m^2 or approx 5,877sq ft) of flat cleared land.

  From Rows 3 & 4 (Center Rows): Dropping straight down to the inverter.

- Approx. 40 ft of wire per string x 2 strings = 80 feet

  From Rows 2 & 5 (Middle-Outer Rows): Must travel ~6.5 ft up/down and ~41 ft sideways to reach the center.

- Approx. 95 ft of wire per string x 3 strings = 285 feet

  From Rows 1 & 6 (Far Edge Rows): Must travel ~13 ft up/down and ~41 ft sideways to reach the center.

- Approx. 110 ft of wire per string x 2 strings = 220 feet

  - USE 125A 3 MAIN AC BREAKER

- Sizing of Inverter

| Table 4.5. Non-Motor Load Surge Power Requirements |  |  |  |
| --- | --- | --- | --- |
| Equipment | Total Power (W) | Factor | Surge Power (W) |
| Light Bulbs (Nursing) | 176 | 1.3 | 228.8 |
| Light Bulbs (USSO) | 680 | 1.3 | 884 |
| Light Bulbs (VPSAS) | 296 | 1.3 | 384.8 |
| Fluorescent Tubes (Nursing) | 1,840 | 1.3 | 2,392.00 |
| Fluorescent Tubes (VPSAS) | 80 | 1.3 | 104 |
| PCs (Nursing) | 800 | 1.3 | 1,040.00 |
| PCs (USSO) | 1,400 | 1.3 | 1,820.00 |
| PCs (VPSAS) | 800 | 1.3 | 1,040.00 |
| Laptops | 400 | 1.3 | 520 |
| Printers (All Buildings) | 354 | 1.3 | 460.2 |
| TVs | 480 | 1.3 | 624 |
| Speakers | 650 | 1.3 | 845 |
| CCTV | 30 | 1.3 | 39 |
| Telephone | 12 | 1.3 | 15.6 |
| Projector | 200 | 1.3 | 260 |
| Coffee Maker (750 W) | 750 | 1.3 | 975 |
| Coffee Maker (550 W) | 550 | 1.3 | 715 |
| Electric Stove (2 units) | 2,400 | 1.3 | 3,120.00 |
| Bread Toaster | 1,500 | 1.3 | 1,950.00 |
| Emergency Lights | 21 | 1.3 | 27.3 |
| Tolago Ceiling Light | 46 | 1.3 | 59.8 |
| Total Non-Motor Surge Power |  |  | 17,503.5 W |

| Equipment | Total Power (W) | Surge Factor | Surge Power (W) |
| --- | --- | --- | --- |
| Inverter Floor Mounted Aircon | 10,800 | 3 | 32,400 |
| Window Type Aircon (Nursing) | 5,100 | 3 | 15,300 |
| Split Type Aircon (Nursing) | 1,500 | 3 | 4,500 |
| Window Type Aircon (USSO) | 8,500 | 3 | 25,500 |
| Split Type Aircon (USSO) | 1,500 | 3 | 4,500 |
| Aircon (VPSAS) | 7,200 | 3 | 21,600 |
| Ceiling Fans | 800 | 3 | 2,400 |
| Electric Fan (300 W) | 300 | 3 | 900 |
| Electric Fans (70 W) | 630 | 3 | 1,890 |
| Stand Fans | 350 | 3 | 1,050 |
| Industrial Fans | 700 | 3 | 2,100 |
| Evaporative Air Cooler | 150 | 3 | 450 |
| Refrigerator (Nursing) | 77 | 3 | 231 |
| Refrigerator (VPSAS) | 130 | 3 | 390 |
| Water Dispensers (Nursing) | 600 | 3 | 1,800 |
| Water Dispensers (USSO) | 600 | 3 | 1,800 |
| Water Dispensers (VPSAS) | 600 | 3 | 1,800 |
| Air Purifier | 80 | 3 | 240 |
| Electric Bed | 100 | 3 | 300 |
| Total Motor Surge Power |  |  | 119,151 W |

- Wire sizing

- Home run wire

VDI = (14 A * 55 ft) / (2% * 940 V) = 770 / 18.8 = 40.9

(Black & Red PV Wire)~700 ft 1 x 1,000 ft Spool (or two 500 ft spools split by color)

need 14 pairs of MC4 or MC4-EVO2 connectors

-700 feet of wire to connect the rows to the inverter, use standard #10 AWG (or #8 AWG) UV-Resistant PV Wire.

- The AC Main Run

VDI = (108.04 A * 50 ft) / (2 * 420 V) = 5402 / 840 = 6.43

-Single 3-Phase cable run of 1/0 AWG or 2/0 AWG Copper (consisting of 3 phase wires + 1 ground) to run from the inverter back to the main 150A or 250A grid breaker.